## DataSIzeAssumptions
Data | Total size (bytes) | Breakdown
Command / Request (data flow to the meter) – request from the Authorised Party for a certain data | 25 | The request can be made to schedule reads, to update meter, to request reads on demand, to control load, to change tariff etc.
Meter Periodic Data read | 4 | Real Power (import) (kW)
| 4 | Reactive Power (import) (kVAr)
| 4 | Real Power (export) (kW)
| 4 | Reactive Energy (export) (kVAr)
| 4 | Micro-generation Real Power (kW)
| 4 | Micro-generation Reactive Power (kVAr)
| 4 | Voltage
| 4 | Power Factor
| 4 | GAS-per read*
Confirmation / Notification message | 25 | Includes: Failure notifications, messages, etc.
Meter sends Error Report | 18 | This report is automatically produced when failure occurs within the system
| 2 | Error Id
| 1 | Switch Status
| 4 | Timestamp
| 4 | read voltage
| 4 | read frequency
| 1 | Report type
| 1 | Check sum
| 1 | Closing flag
Meter sends Performance Report | 150 | This report is produced on occurrence of the failure or as scheduled to determine meter performance.
| 1 | Status
| 4 | Timestamp
| 2 | Diagnostics
| 1 | Report type
| 140 | Event Log (14 bytes per event) - assumed 10 events
| 1 | Check sum
| 1 | Closing flag
Meter sends Outage Report (1 outage registered) | 14 | Outage report is sent after the supply has been restored
| 4 | Outage detected timestamp
| 4 | Supply restored timestamp
| 2 | Event id
| 4 | Data
Weekly read submission | 28 | 7*8 (for electricity)
| 28 | 7*4 (for gas)
One month worth of data (assumed to include Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data) | 40320 | (4*48*30)*7
Last day HH import data summary | 192 | 48*4
CV value for gas | 8
Event | 14
Security Assumptions:
Security | 22 | bytes
Packet Frame Overhead Assumptions
Protocols: | Estimated Protocol frame size (bytes)
Transport Protocols:
IEC 61334 (S-FSK, FSK, OFDM) | 45
IEC 62056-31 Euridis[3] | 45
EN 13757 M-Bus[7] | 27
TCP/IP protocol[8] | 50
SITRED[11] | 45
PRIME | 8
Zigbee | 15
EverBlu | unknown
OPERA/UPA[16] | 24
Data Exchange Protocols
IEC 62056-21”FLAG” | 22
IEC 62056 DLMS/COSEM[5] | 14
SML[9] | 14
Zigbee SmartEnergy | 25
OPERA/UPA[16] | 24
Communication Transaction Overhead Assumption
TCP/IP based communication | 500 | (bytes)
Table 2 – Summary of data size assumptions

## EleTransferFrequencyAssumptions
Electricity
| Type of data | Data granularity registered at the meter | Intervals per day | Data transmission granularity | Data reads days before transmission | Frequency of data transmission per year
Assessment of network performance
Use Case 01 - Monitor Power flows and voltage levels to identify thermal capacity and statutory voltage headroom
1. Data is periodically sent from the Smart Metering System | Real Power (import) (kW) | HH average | 48 | 3 months | 92 | 4
| Reactive Power (import) (kVAr) | HH average | 48 | 3 months | 92 | 4
| Real Power (export) (kW) | HH average | 48 | 3 months | 92 | 4
| Reactive Energy (export) (kVAr) | HH average | 48 | 3 months | 92 | 4
| Micro-generation Real Power (kW) | HH average | 48 | 3 months | 92 | 4
| Micro-generation Reactive Power (kVAr) | HH average | 48 | 3 months | 92 | 4
| Voltage | HH average | 48 | 3 months | 92 | 4
| Power Factor | HH average | 48 | 3 months | 92 | 4
2. DNO requests data | Command to send data | on event (assumed once every 3 months) | 1 | 3 months | 1 | 4
3. The Smart Metering System sends the requested data | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | on event (assumed once every 3 months) | 1 | 3 months | 1 | 4
Alternative Flow:
1. Smart Metering System rejects the message as invalid | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
2. The Smart Metering System does not have any measured data stored | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Request for weekly reads | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Weekly read submission | on event (assumed once a year) | 1 | once a year | 1 | 1
3.1 The DNO does not receive the data from the Smart Metering System (scenario 1) | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
3.2 The DNO does not receive the data from the Smart Metering System (scenario 2) | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
Use Case 02 - Determine network impact of proposed new demand / generation connections
1. DNO requests stored HH power flow and voltage data (and micro-generation data where available) | Command to send data | on event (assumed once every 3 months) | 1 | 3 months | 1 | 4
2. Smart Metering System retrieves the requested data | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | on event (assumed once every 3 months) | 1 | 3 months | 1 | 4
Alternative Flow:
1. The DNO does not receive the data | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
Use Case 03 - Determine network impact of proposed increase in demand / generation at existing connection points
1. DNO requests stored HH power flow and voltage data (and micro-generation data where available) | Command to send data | on event (assumed once every 3 months) | 1 | 3 months | 1 | 4
2. Smart Metering System retrieves the requested data | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | on event (assumed once every 3 months) | 1 | 3 months | 1 | 4
Alternative Flow:
1. The DNO does not receive the data | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
Use Case 04 - Monitor demand and generation profiles for network load forecasting
1. At the defined interval the Smart Metering System collects the data and sends it to the DNO (please see Use Case 01 scenario 1 and alternate flow 4)
Use Case 05 - Determine Latent Demand due to Embedded Generation
1. At the defined interval the Smart Metering System collects the data and sends it to the DNO (please see Use Case 01 scenario 1 and alternate flow 4)
Use Case 06 - Identify Voltage Quality Issues
1. The Smart Metering System accumulates time and data stamped voltage quality events (assumed 6 events) | Meter sends event report | on event (assumed once a month) | 1 | On event (assumed every 6 months) | 6 | 2
Alternative Flow:
1. Meter fails to send the message | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
Actively manage network
Use Case 07 - Collect data for active management
1. Data is periodically sent from the Smart Metering System (import/export; real/reactive flow, real/reactive generation flow and voltage as specified by DNOs) as in Use Case 01 Scenario 1
Alternative Flow:
1. Meter fails to send the message | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
08 Use Case - Active network management of network voltage
The same data flow as in Use Case 09
09 Use Case - Perform Active Management of Network Power Flow
1. Operation of (Distribution Use of System) Time of Use tariff | TOU tariffs configured | on occurrence (assumed to happen every 3 months) | 1 | 3 months | 1 | 4
| Notification of new TOU | on occurrence (assumed to happen every 3 months) | 1 | 3 months | 1 | 4
| TOU readings provided to DNO's (assumed summer tariff- daily reads for 60 days) | on occurrence (assumed to happen every 3 months) | 1 | 3 months | 1 | 4
2. Operation of (Distribution Use of System) Real Time Pricing | Real time tariff notification sent | on occurrence (assumed to happen every 3 months) | 1 | 3 months | 1 | 4
| Notification of new TOU | on occurrence (assumed to happen every 3 months) | 1 | 3 months | 1 | 4
3. Power Sharing by Maximum Thresholds | Notification of "load exceeded" sent | on occurrence (assumed to happen every 3 months) | 1 | 3 months | 1 | 4
| Notification "load within acceptable limits" | on occurrence (assumed to happen every 3 months) | 1 | 3 months | 1 | 4
4. Direct Control, by DNOs, of appliance or micro-generation | Command to control (disconnect) the appliance or disable supply | on occurrence (assumed to happen every 3 months) | 1 | 3 months | 1 | 4
| Command to reconnect the appliance or enable the supply | on occurrence (assumed to happen every 3 months) | 1 | 3 months | 1 | 4
Alternative Flow:
1. Maximum Power Threshold Reached - consumer does not turn off appliances | Notification of "load exceeded" sent | on occurrence (assumed to happen every 3 months) | 1 | 3 months | 1 | 4
2. Power Sharing by Maximum Power Thresholds - consumer turns off some of the appliances | Notification of "load exceeded" sent | on occurrence (assumed to happen every 3 months) | 1 | 3 months | 1 | 4
| Notification "load within acceptable limits" | on occurrence (assumed to happen every 3 months) | 1 | 3 months | 1 | 4
The same data flow as in Use Case 09
System Balancing
10 Use Case - Perform System Balancing
The same data flow as in Use Case 09
11 Use Case - Check effectiveness of active network management / system balancing measures
1. The Smart Metering System measures power flow and voltage data (as in Use Case 01 scenario 01)
2. DNO requests data | Command to send data | on event (assumed once every 3 months) | 1 | 3 months | 1 | 4
3. The Smart Metering System sends the requested data | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | on event (assumed once every 3 months) | 1 | 3 months | 1 | 4
Alternative Flow:
1. Meter fails to send the message | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
Actively manage network during planned and unplanned Outage
Use Case 12 - Notify consumer of planned outage
1. Consumer notification of planned / emergency outage | Notification sent (10 days in advance) | on event (assumed once a year) | 1 | once a year | 1 | 1
| Notification sent (outage is due to begin- 1 hour before the event) | on event (assumed once a year) | 1 | once a year | 1 | 1
2. Consumer notified that outage is over | Notification the outage is over | on event (assumed once a year) | 1 | once a year | 1 | 1
Alternative Flow:
1. Smart Metering System deems the request invalid for scenario 1 | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
2. DNOs do not receive akcnowledgment message for scenario 1 | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
3. Smart Metering System deems the request invalid for scenario 2 | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
4. DNOs do not receive akcnowledgment message for scenario 2 | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
Use Case 13 - Query Meter Energisation Status to determine Outage Source and Location
1. False Outage Report (DNO checks meter energisation status: supply on) | Energisation status "supply on" submitted | On event (assumed once a year) | 1 | once a year | 1 | 1
| Request for switch status | On event (assumed once a year) | 1 | once a year | 1 | 1
| Response | On event (assumed once a year) | 1 | once a year | 1 | 1
2. Confirmed network outage | Request for energisation status | On event (assumed once a year) | 1 | once a year | 1 | 1
| Energisation status "supply off" submitted | On event (assumed once a year) | 1 | once a year | 1 | 1
Alternative Flow:
1. Smart Metering deems the request invalid (for scenario 1) | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
2. DNO does not receive the message (scenario 1) | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
Use Case 14 - Send Alarm to DNO during network outage
1. Outage alarm sent to the Distribution Network Operator | Outage alarm sent | On event (assumed once a year) | 1 | once a year | 1 | 1
Alternative Flow:
1. Smart Metering System is unable to send the outage alarm message | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
2. DNO does not receive notification | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
Use Case 15 - Verify restoration of supplies after outage
1. Meter notifies DNOs of power restoration | "Power restored" notification | On event (assumed every 6 months) | 1 | 6 months | 1 | 2
Alternative Flow:
1. Smart Metering System fails to detect power restoration | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
2. DNO does not receive notification | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
Use Case 16 - Regulatory Reporting of outages
1. DNO requests stored outage information | Command to send data | on event (assumed once every 3 months) | 1 | 3 months | 1 | 4
2. Meter sends outage report | Outage report sent | on event (assumed every 3 months) | 1 | 3 months | 1 | 4
Alternative Flow:
1. Smart Metering rejects the message as invalid | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
2. Smart Metering System does not have any of the requested information stored | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Request for weekly reads | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Weekly read submission | on event (assumed once a year) | 1 | once a year | 1 | 1
3. DNO does not receive notification | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
Use Case 17 - Restore and maintain supply during outages
1. Smart Metering System sends "power restored" message to the DNO | "Power restored" notification | On event (assumed every 6 months) | 1 | 6 months | 1 | 2
2. DNO activates the maximum power consumption threshold | Command to active power threshold | On event (assumed every 6 months) | 1 | 6 months | 1 | 2
3. Smart Metering confirms activation of the maximum power consumption threshold | Confirmation sent | On event (assumed every 6 months) | 1 | 6 months | 1 | 2
Alternative Flow:
1. DNO does not receive "power restored" message | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
2. Smart Metering deems the request invalid | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
3. DNO does not receive the confirmation response | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
Manage safety issues
Use Case 18 - Manage meter safety alarm
1. Smart Metering System sends alarm to DNOs | Alarm sent | On event (assumed once a year) | 1 | once a year | 1 | 1
2. DNO remotely disconnects the supply through the Smart Metering System (where necessary) | Disconnection command | on event (assumed once a year) | 1 | once a year | 1 | 1
3. The Smart Metering sends the confirmation message to the DNO | Confirmation sent | on event (assumed once a year) | 1 | once a year | 1 | 1
Alternative Flow:
1. DNO does not receive the alarm | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
2. Smart Metering deems the request invalid | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
3. DNO does not receive confirmation of the supply switch activating to cut-off supply | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
Use Case 19 - Manage extreme voltage at meter
1. The Smart Metering System sends alarm of a voltage level outside its ocnfigured tolerance levels | Alarm sent | On event (assumed to happen once every 6 months) | 1 | 6 months | 1 | 2
2. (Optionally) the Smart Metering System auto-disconnects itself from the network supply of electricity sending confirmation of disconnection to the DNO | Supply disabled | on event (assumed once a year) | 1 | once a year | 1 | 1
3. Supply is enabled by DNO after emergency/safety action | Supply enabled | on event (assumed once a year) | 1 | once a year | 1 | 1
Alternative Flow:
1. The Smart Metering System fails to send the extreme voltage alarm | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
2. The Smart Metering System fails to auto disconnect | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
Support network activities
Use Case 20 - Configure Smart Metering System
1. DNO configures meter reading registers | DNO configures meter reading register | on event (assumed every 3 years) | 1 | every 3 years | 1 | 1
| Confirmation sent | on event (assumed every 3 years) | 1 | every 3 years | 1 | 1
2. DNO configures meter alarms | DNO configures meter alarms | on event (assumed every 3 years) | 1 | every 3 years | 1 | 1
| Confirmation sent | on event (assumed every 3 years) | 1 | every 3 years | 1 | 1
3. DNO configures meter load threshold | DNO configures load threshold | on event (assumed every 3 years) | 1 | every 3 years | 1 | 1
| Confirmation sent | on event (assumed every 3 years) | 1 | every 3 years | 1 | 1
Alternative Flow:
1. Smart Metering deems the request invalid | Failure notification | on event (assumed every 3 years) | 1 | every 3 years | 1 | 1
| Error Report | on event (assumed every 3 years) | 1 | every 3 years | 1 | 1
2. DNOs do not receive notification | Failure notification | on event (assumed every 3 years) | 1 | every 3 years | 1 | 1
| Error Report | on event (assumed every 3 years) | 1 | every 3 years | 1 | 1
| Test request | on event (assumed every 3 years) | 1 | every 3 years | 1 | 1
| Performance report | on event (assumed every 3 years) | 1 | every 3 years | 1 | 1
| Service restored notification | on event (assumed every 3 years) | 1 | every 3 years | 1 | 1

## Gas_TransferFreqAssumpt
| Type of data | Data granularity registered at the meter | Intervals per day | Data transmission granularity | Data reads days before transmission | Frequency of data transmission per year
Use Case 1 - Gather information for planning
1. The Smart Metering System sends the recorded gas demand data to the GDNO (6min) | Interval Gas values | Every 6 minutes all day for the winter period (November-March) | 240 | once a year | 182.5 | 1
|  | Every 6 minutes in summer (June-September) all day | 240 | once a year | 182.5 | 1
2. The Smart Metering System sends the recorded gas demand data to the GDNO (daily) | Daily Gas values | every day at 6 am | 1 | every 6 months | 182.5 | 2
Alternative Flow:
1. Meter does not communicate requested data to the authorised GDN party | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
2. Meter data reads are missing / corrupted | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Test request | on event (assumed once a year) | 1 | once a year | 1 | 1
| Performance report | on event (assumed once a year) | 1 | once a year | 1 | 1
| Request for weekly reads | on event (assumed once a year) | 1 | once a year | 1 | 1
| Service restored notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Weekly read submission | on event (assumed once a year) | 1 | once a year | 1 | 1
Use Case 02 - Configure Gas Smart Metering System
1. GDN configures meter reading registers | GDN configure meter reading register | on event (assumed to happen every 3 years) | 1 | every 3 years | 1 | 1
| Confirmation sent | on event (assumed to happen every 3 years) | 1 | every 3 years | 1 | 1
| GDN configure meter alarms | on event (assumed to happen every 3 years) | 1 | every 3 years | 1 | 1
| Confirmation sent | on event (assumed to happen every 3 years) | 1 | every 3 years | 1 | 1
Alternative Flow:
1. Smart Metering deems the request invalid | Failure notification | on event (assumed once every 3 years) | 1 | every 3 years | 1 | 1
| Error Report | on event (assumed once every 3 years) | 1 | every 3 years | 1 | 1
2. GDNs do not receive confirmation | Failure notification | on event (assumed to happen every 3 years) | 1 | every 3 years | 1 | 1
| Error Report | on event (assumed to happen every 3 years) | 1 | every 3 years | 1 | 1
| Test request | on event (assumed to happen every 3 years) | 1 | every 3 years | 1 | 1
| Performance report | on event (assumed to happen every 3 years) | 1 | every 3 years | 1 | 1
| Service restored notification | on event (assumed to happen every 3 years) | 1 | every 3 years | 1 | 1
Use Case 03 - Disable Supply of Gas by GDN
1. Gas is disabled by GDNs | GDN disables gas supply | on event (assumed once every 3 years) | 1 | every 3 years | 1 | 1
| Meter sends confirmation | on event (assumed once every 3 years) | 1 | every 3 years | 1 | 1
| GDN enable gas supply | on event (assumed once every 3 years) | 1 | every 3 years | 1 | 1
Alternative Flow:
GDNs do not receive confirmation | Failure notification | on event (assumed once every 3 years) | 1 | every 3 years | 1 | 1
| Error Report | on event (assumed once every 3 years) | 1 | every 3 years | 1 | 1
| Test request | on event (assumed once every 3 years) | 1 | every 3 years | 1 | 1
| Performance report | on event (assumed once every 3 years) | 1 | every 3 years | 1 | 1
| Service restored notification | on event (assumed once every 3 years) | 1 | every 3 years | 1 | 1
Smart Metering deems the request invalid | Failure notification | on event (assumed once every 3 years) | 1 | every 3 years | 1 | 1
| Error Report | on event (assumed once every 3 years) | 1 | every 3 years | 1 | 1
Use Case 04 - Display Messages from Gas Distribution Network
GDN sends notification to IHD | GDN send message to IHD | on event (assumed once every 10 years) | 1 | every 10 years | 1 | 1
| meter acknowledges | on event (assumed once every 10 years) | 1 | every 10 years | 1 | 1
Alternative Flow:
Meter fails to send confirmation message | Failure notification | on occurrence | 1 | on event | 1 | 1
| Error Report | on occurrence | 1 | on event | 1 | 1
| Test request | on occurrence | 1 | on event | 1 | 1
| Performance report | on occurrence | 1 | on event | 1 | 1
| Service restored notification | on occurrence | 1 | on event | 1 | 1
Use Case 05 - Measure and Store Calorific Values at the meter
| CV value for the day | daily | 1 | daily | 1 | 365
| Confirmation | daily | 1 | daily | 1 | 365
(Optionally) GDN update the message | Updated CV value for the day | on occurrence (assumed to happen once a month) | 1 | monthly | 1 | 12
| Confirmation | monthly | 1 | monthly | 1 | 12
Alternative Flow:
1. The Smart Metering System rejects the message as invalid | Failure notification | on event (assumed once a year) | 1 | once a year | 1 | 1
| Error Report | on event (assumed once a year) | 1 | once a year | 1 | 1
| GDN resends the message | on event (assumed once a year) | 1 | once a year | 1 | 1
| Confirmation | on event (assumed once a year) | 1 | once a year | 1 | 1
Tampering Notification send to GDNs
| Meter sends tampering notification | on event (assumed once a year) | 1 | once a year | 1 | 1

## Electricity_DataTraffic
|  |  | Electricity related data flows | [8 empty] | TCP/IP protocol data traffic
| Raw Total per meter per operation (bytes) | Type of data | Raw Data size (bytes) | Data granularity registered at the meter | Data flow from | Data transmission granularity | Data transmitted to: | ENA Latency req. (command execution time) | Raw size of data prior to transmission (bytes) |  | Data+ security (22 bytes) | TCP/IP packet + overhead per packet (Data+ 50 bytes) | TCP/IP data transmission overheads (data + 500) bytes | Cumulative per activity (bytes) | Data volume per year
Assessment of network performance | [8 empty] | Formula | Total | 22 | 50 | 500 |  | Bytes per year | Cumulative per year
Use Case 01 - Monitor current flows and voltage levels to identify thermal capacity and statutory voltage headroom
1. Data is periodically sent from the Smart Metering System (Scenario 1) | 32 | Real Power (import) (kW) | 4 | HH average | SM | 3 months | CCP | on availability | 4x48x92 | 17664 | 17686 | 17736 | 18236 | 18236 | 72944 | 72944
|  | Reactive Power (import) (kVAr) | 4 | HH average | SM | 3 months | CCP | on availability | 8x48x92 | 17664 | 17686 | 17736 | 18236 | 36472 | 72944 | 145888
|  | Real Power (export) (kW) | 4 | HH average | SM | 3 months | CCP | on availability | 4x48x92 | 17664 | 17686 | 17736 | 18236 | 54708 | 72944 | 218832
|  | Reactive Energy (export) (kVAr) | 4 | HH average | SM | 3 months | CCP | on availability | 4x48x92 | 17664 | 17686 | 17736 | 18236 | 72944 | 72944 | 291776
|  | Micro-generation Real Power (kW) | 4 | HH average | SM | 3 months | CCP | on availability | 4x48x92 | 17664 | 17686 | 17736 | 18236 | 91180 | 72944 | 364720
|  | Micro-generation Reactive Power (kVAr) | 4 | HH average | SM | 3 months | CCP | on availability | 4x48x92 | 17664 | 17686 | 17736 | 18236 | 109416 | 72944 | 437664
|  | Voltage | 4 | HH average | SM | 3 months | CCP | on availability | 4x48x92 | 17664 | 17686 | 17736 | 18236 | 127652 | 72944 | 510608
|  | Power Factor | 4 | HH average | SM | 3 months | CCP | on availability | 4x48x92 | 17664 | 17686 | 17736 | 18236 | 145888 | 72944 | 583552 | 142.4688 |  | 583552
2. DNO requests data (Scenario 2) | 25 | Command to send data | 25 | once every 3 months | DNO | 3 months | SM | 12 hours | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 2388 | 2388
3. The Smart Metering System sends the requested data (Scenario 2) | 40320 | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | 40320 | once every 3 months | SM | 3 months | DNO |  | 40320x1 | 40320 | 40342 | 40392 | 40892 | 41489 | 163568 | 165956 |  |  | 165956
Alternative Flow:
1. Smart Metering System rejects the message as invalid | 43 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18 x 1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
2. The Smart Metering System does not have any measured data stored | 296 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Request for weekly reads | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3700 | 597 | 3700
|  | Weekly read submission | 28 | on event (assumed once a year) | SM | once a year | CCP |  | 56x1 | 28 | 50 | 100 | 600 | 4300 | 600 | 4300
3.1 The DNO does not receive the data from the Smart Metering System (for scenario 1) | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
3.2 The DNO does not receive the data from the Smart Metering System (for scenario 2) | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
Use Case 02 - Determine network impact of proposed new demand / generation connections
1. DNO requests stored HH power flow and voltage data (and micro-generation data where available) | 40345 | Command to send data | 25 | on event (assumed once every 3 months) | DNO | 3 months | SM |  | 25x1 | 25 | 47 | 97 | 597 | 597 | 2388 | 2388
2. Smart Metering System retrieves the requested data |  | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | 40320 | on event (assumed once every 3 months) | SM | 3 months | DNO | 12 hours | 40320x1 | 40320 | 40342 | 40392 | 40892 | 41489 | 163568 | 165956 |  |  | 165956
Alternative Flow:
1. The DNO does not receive the data | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
Use Case 03 - Determine network impact of proposed increase in demand / generation at existing connection points
1. DNO requests stored HH power flow and voltage data (and micro-generation data where available) | 40345 | Command to send data | 25 | on event (assumed once every 3 months) | DNO | 3 months | SM |  | 25x1 | 25 | 47 | 97 | 597 | 597 | 2388 | 2388
2. Smart Metering System retrieves the requested data |  | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | 40320 | on event (assumed once every 3 months) | SM | 3 months | DNO | 12 hours | 40320x1 | 40320 | 40342 | 40392 | 40892 | 41489 | 163568 | 165956 |  |  | 165956
Alternative Flow:
1. The DNO does not receive the data | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
Use Case 04 - Monitor demand and generation profiles for network load forecasting
1. At the defined interval the Smart Metering System collects the data and sends it to the DNO (please see Use Case 01 scenario 1 and alternate flow 4)
Use Case 05 - Determine Latent Demand due to Embedded Generation
1. At the defined interval the Smart Metering System collects the data and sends it to the DNO (please see Use Case 01 scenario 1 and alternate flow 4)
Use Case 06 - Identify Voltage Quality Issues
1. The Smart Metering System accumulates time and data stamped voltage quality events (assumed 6 events) | 14 | Meter sends event report | 14 | on event (assumed once a month) | SM | On event (assumed every 6 months) | DNO | 12 hours | 14x1 | 84 | 106 | 156 | 656 | 656 | 1312 | 1312 |  |  | 1312 | 6 mths
Alternative Flow:
1. Meter fails to send the message | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
Actively manage network / System Balancing
Use Case 07 - Collect data for active management
1. Data is periodically sent from the Smart Metering System (import/export; real/reactive flow, real/reactive generation flow and voltage as specified by DNOs) as in Use Case 01 Scenario 1
Alternative Flow:
1. Meter fails to send the message | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
08 Use Case - Active network management of network voltage (Active network management of network voltage – Uses Voltage information captured to instigate actions on DNO Assets to control voltage, as well as having the same data flows as Use Case 09 to undertake actions in the household to address voltage issues via ToU/Peak tariffs, control household equipment etc.
The same data flow as in Use Case 09
09 Use Case - Perform Active Management of Network Power Flow
1. Operation of (Distribution Use of System) Time of Use tariff | 290 | TOU tariffs configured | 25 | on occurrence (assumed to happen every 3 months) | DNO | 3 months | SM | 5-15 min. | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 2388 | 2388
|  | Notification of new TOU | 25 | on occurrence (assumed to happen every 3 months) | SM | 3 months | IHD |  | 25 x 1 | 25 | 47 | 97 | 597 | 1194 | 2388 | 4776
|  | TOU readings provided to DNO's (assumed summer tariff- daily reads for 60 days) | 240 | on occurrence (assumed to happen every 3 months) | SM | 3 months | DNO | 12 hours | 240 x 1 | 240 | 262 | 312 | 812 | 2006 | 3248 | 8024 |  |  | 8024
2. Operation of (Distribution Use of System) Real Time Pricing | 50 | Real time tariff notification sent | 25 | on occurrence (assumed to happen every 3 months) | DNO | 3 months | SM | 5-15 min. | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 2388 | 2388
|  | Notification of new TOU | 25 | on occurrence (assumed to happen every 3 months) | SM | 3 months | IHD |  | 25 x 1 | 25 | 47 | 97 | 597 | 1194 | 2388 | 4776 |  |  | 4776
3. Power Sharing by Maximum Thresholds | 50 | Notification of "load exceeded" sent | 25 | on occurrence (assumed to happen every 3 months) | SM | 3 months | IHD |  | 25 x 1 | 25 | 47 | 97 | 0 | NA | NA | NA
|  | Notification "load within acceptable limits" | 25 | on occurrence (assumed to happen every 3 months) | SM | 3 months | IHD |  | 25 x 1 | 25 | 47 | 97 | 0 | NA | NA | NA
4. Direct Control, by DNOs, of appliance or micro-generation | 50 | Command to control (disconnect) the appliance or disable supply | 25 | on occurrence (assumed to happen every 3 months) | DNO | 3 months | SM | 5-15 min. | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 2388 | 2388
|  | Command to reconnect the appliance or enable the supply | 25 | on occurrence (assumed to happen every 3 months) | DNO | 3 months | SM | 5-15 min. | 25 x 1 | 25 | 47 | 97 | 597 | 1194 | 2388 | 4776 |  |  | 4776
Alternative Flow:
1. Maximum Power Threshold Reached - consumer does not turn off appliances | 25 | Notification of "load exceeded" sent | 25 | on occurrence (assumed to happen every 3 months) | SM | 3 months | IHD | 5-15 min. | 25 x 1 | 25 | 47 | 97 | 0 | NA | NA | NA
2. Power Sharing by Maximum Power Thresholds - consumer turns off some of the appliances | 50 | Notification of "load exceeded" sent | 25 | on occurrence (assumed to happen every 3 months) | SM | 3 months | IHD |  | 25 x 1 | 25 | 47 | 97 | 0 | NA | NA | NA
|  | Notification "load within acceptable limits" | 25 | on occurrence (assumed to happen every 3 months) | SM | 3 months | IHD |  | 25 x 1 | 25 | 47 | 97 | 0 | NA | NA | NA
System Balancing
10 Use Case - Perform System Balancing
The same data flow as in Use Case 09
11 Use Case - Check effectiveness of active network management / system balancing measures
1. The Smart Metering System measures power flow and voltage data (as in Use Case 01 scenario 01)
2. DNO requests data | 40345 | Command to send data | 25 | on occurrence (assumed to happen once every 3 months) | DNO | 3 months | SM | 5-15min. | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 2388 | 2388
3. The Smart Metering System sends the requested data |  | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | 40320 | on occurrence (assumed to happen once every 3 months) | SM | 3 months | DNO | 15 min. | 40320 x 1 | 40320 | 40342 | 40392 | 40892 | 41489 | 163568 | 165956 |  |  | 165956
Alternative Flow:
1. Meter fails to send the message | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
Actively manage network during planned and unplanned Outage
Use Case 12 - Notify consumer of planned outage
1. Consumer notification of planned / emergency outage | 50 | Notification sent (10 days in advance) | 25 | on occurrence of the event (assumed to happen once per year) | DNO | once per year | SM | Message confirmation within 12 hours. | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Notification sent (outage is due to begin- 1 hour before the event) | 25 | on occurrence of the event (assumed to happen once per year) | DNO | once per year | SM | 5-10 min. | 25 x 1 | 25 | 47 | 97 | 597 | 1194 | 597 | 1194
2. Consumer notified that outage is over | 25 | Notification the outage is over | 25 | on occurrence of the event (assumed to happen once per year) | DNO | once per year | SM | 5-10 min. | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 1791 | 1791 |  | 1791 | once per year
Alternative Flow:
1. Smart Metering System deems the request invalid for scenario 1 | 43 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18 x 1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
2. DNOs do not receive akcnowledgment message for scenario 1 | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
3. Smart Metering System deems the request invalid for scenario 2 | 43 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597 | 1187
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18 x 1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
4. DNOs do not receive akcnowledgment message for scenario 2 | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103 | 8580 | 8580
Use Case 13 - Query Meter Energisation Status to determine Outage Source and Location
1. False Outage Report (DNO checks meter energisation status: supply on) | 75 | Energisation status "supply on" submitted | 25 | On occurrence of the event (assumed to happen once per year) | SM | once a year | DNO | 1,000 meters in 15 min. or 100,000 in 1 hour; in cases of extreme weather events 30 sec per meter | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Request for switch status | 25 | On occurrence of the event (assumed to happen once per year) | DNO | once a year | SM |  | 25 x 1 | 25 | 47 | 97 | 597 | 1194 | 597 | 1194
|  | Response | 25 | On occurrence of the event (assumed to happen once per year) | SM | once a year | DNO |  | 25 x 1 | 25 | 47 | 97 | 597 | 1791 | 597 | 1791 |  |  | 1791 | once per year
2. Confirmed network outage | 50 | Request for energisation status | 25 | On occurrence of the event (assumed to happen once per year) | DNO | once a year | SM | 1,000 meters in 15 min. or 100,000 in 1 hour; in cases of extreme weather events 30 sec per meter | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Energisation status "supply off" submitted | 25 | On occurrence of the event (assumed to happen once per year) | SM | once a year | DNO |  | 25 x 1 | 25 | 47 | 97 | 597 | 1194 | 597 | 1194 |  |  | 1194 | once per year
Alternative Flow:
1. Smart Metering deems the request invalid (for scenario 1) | 43 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18 x 1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
2. DNO does not receive the message (scenario 1) | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103 | 4290 | 4290
Use Case 14 - Send Alarm to DNO during network outage
1. Outage alarm sent to the Distribution Network Operator | 25 | Outage alarm sent | 25 | On occurrence of the event (assumed to happen once per year) | SM | once a year | DNO | Up to 15min. | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597 |  |  | 597 | once per year
Alternative Flow:
1. Smart Metering System is unable to send the outage alarm message | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
2. DNO does not receive notification | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
Use Case 15 - Verify restoration of supplies after outage
1. Meter notifies DNOs of power restoration | 25 | "Power restored" notification | 25 | On occurrence of the event (assumed to happen once every 6 months) | SM | 6 months | DNO | Up to15 min. | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 1194 | 1194 |  |  | 1194 | twice p.a.
Alternative Flow:
1. Smart Metering System fails to detect power restoration | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
DNOs do not receive notification | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
Use Case 16 - Regulatory Reporting of outages
1. DNO requests stored outage information | 39 | Command to send data | 25 | on event (assumed once every 3 months) | SM | 3 months | DNO | 12 hours | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 2388 | 2388
2. Meter sends outage report |  | Outage report sent | 14 | on event (assumed once every 3 months) | SM | 3 months | DNO | 12 hours | 14 x 1 | 14 | 14 | 64 | 564 | 1161 | 2256 | 4644 |  |  | 4644
Alternative Flow:
1. Smart Metering rejects the message as invalid | 43 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18 x 1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
2. Smart Metering System does not have any of the requested information stored | 296 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Request for weekly reads | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3700 | 597 | 3700
|  | Weekly read submission | 28 | on event (assumed once a year) | SM | once a year | CCP |  | 56x1 | 28 | 50 | 100 | 600 | 4300 | 600 | 4300
3. DNO does not receive notification | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
Use Case 17 - Restore and maintain supply during outages
1. Smart Metering System sends "power restored" message to the DNO | 25 | "Power restored" notification | 25 | On occurrence of the event (assumed to happen once every 6 months) | SM | 6 months | DNO | 5 min. | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 1194 | 1194
2. DNO activates the maximum power consumption threshold | 25 | Command to active power threshold | 25 | On event (assumed every 6 months) | DNO | 6 months | SM | 15 min. | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 1194 | 1194
3. Smart Metering confirms activation of the maximum power consumption threshold |  | Cobfirmation sent | 25 | On event (assumed every 6 months) | SM | 6 months | DNO |  | 25x1 | 25 | 47 | 97 | 597 | 1194 | 1194 | 2388 |  |  | 3582
Alternative Flow:
1. DNO does not receive "power restored" message | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
2. Smart Metering deems the request invalid | 43 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18 x 1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
3. DNO does not receive the confirmation response | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
Manage safety issues
Use Case 18 - Manage meter safety alarm
1. Smart Metering System sends alarm to DNOs | 25 | Alarm sent | 25 | on event (assumed once a year) | SM | once a year | DNO | 15 min | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597 |  |  | 597
2. DNO remotely disconnects the supply through the Smart Metering System (where necessary) | 50 | Disconnection command | 25 | on event (assumed once a year) | DNO | once a year | SM | 15 min. | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
3. The Smart Metering sends the confirmation message to the DNO |  | Confirmation sent | 25 | on event (assumed once a year) | SM | once a year | DNO |  | 25x1 | 25 | 47 | 97 | 597 | 1194 | 597 | 1194 |  |  | 1194
Alternative Flow:
1. DNO does not receive the alarm | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
2. Smart Metering deems the request invalid | 43 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18 x 1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
3. DNO does not receive confirmation of the supply switch activating to cut-off supply | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
Use Case 19 - Manage extreme voltage at meter
1. The Smart Metering System sends alarm of a voltage level outside its ocnfigured tolerance levels | 75 | Alarm sent | 25 | On occurrence of the event (assumed to happen once every 6 months) | SM | 6 months | DNO | Alarm in up to 15 min. | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 1194 | 1194
2. (Optionally) the Smart Metering System auto-disconnects itself from the network supply of electricity sending confirmation of disconnection to the DNO |  | Supply disabled | 25 | on event (assumed once a year) | DNO | once a year | SM | 5 min. | 25 x 1 | 25 | 47 | 97 | 597 | 1194 | 597 | 1791
3. Supply is enabled by DNO after emergency/safety action |  | Supply enabled | 25 | on event (assumed once a year) | DNO | once a year | SM | 5min. | 25 x 1 | 25 | 47 | 97 | 597 | 1791 | 597 | 2388 |  |  | 2388
Alternative Flow:
1. The Smart Metering System fails to send the extreme voltage alarm | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
2. The Smart Metering System fails to auto disconnect | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
Support network activities
Use Case 20 - Configure Smart Metering System
1. DNO configures meter reading registers | 150 | DNO configure meter reading register | 25 | on event (assumed every 3 years) | DNO | every 3 years | SM | Assumed 15 minutes up to 12 hours (i.e. confirming meter changes) | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Confirmation sent | 25 | on event (assumed every 3 years) | SM | every 3 years | DNO |  | 25x1 | 25 | 47 | 97 | 597 | 1194 | 597 | 1194 |  |  | 1194
2. DNO configures meter alarms |  | DNO configure meter alarms | 25 | on event (assumed every 3 years) | DNO | every 3 years | SM |  | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Confirmation sent | 25 | on event (assumed every 3 years) | SM | every 3 years | DNO |  | 25x1 | 25 | 47 | 97 | 597 | 1194 | 597 | 1194 |  |  | 1194
3. DNO configures meter load threshold |  | DNO configure load threshold | 25 | on event (assumed every 3 years) | DNO | every 3 years | SM |  | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Confirmation sent | 25 | on event (assumed every 3 years) | SM | every 3 years | DNO |  | 25x1 | 25 | 47 | 97 | 597 | 1194 | 597 | 1194 |  |  | 1194
Alternative Flow:
1. Smart Metering deems the request invalid | 43 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18 x 1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
2. DNOs do not receive notification | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, DNO | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103 | Per Meter |  | 27 | Million
TOTAL per meter - everything works well | [9 empty] | 303880 | 305024 | 307674 |  | 332980 |  | 1287624 | 1257.4453 | 1.228 | 32378.2191 | 31.6194
TOTAL per meter - everything fails once | [9 empty] | 310262 | 314574 | 324424 |  | 419342 |  | 1375180 | 1342.9492 | 1.3115 | 34579.8768 | 33.7694
[17 empty] | kbytes | Mbytes | Gbytes | Tbytes
[14 empty] | 325.1758 | 0.31755
[14 empty] | 409.5137 | 0.39992 |  |  | 1.5 | 39550.7812 | 38.6238
[14 empty] | kbytes | Mbytes
[14 empty] | 419112 |  | 1380670
[14 empty] | 230 |  | -5490
Note on N88: Tom Hainey - Engage Consulting Ltd: not related to DNO
Note on N89: Tom Hainey - Engage Consulting Ltd: not related to DNO
Note on N90: Tom Hainey - Engage Consulting Ltd: not related to DNO0
Note on N83: Tom Hainey - Engage Consulting Ltd: not related to DNO
Note on N84: Tom Hainey - Engage Consulting Ltd: not related to DNO

## Gas_DataTraffic
|  |  | Gas related data flows | [8 empty] | TCP/IP protocol data traffic
| Raw Total per meter per operation (bytes) | Type of data | Raw Data size (bytes) | Data granularity registered at the meter | Data flow from | Data transmission granularity | Data transmitted to: | ENA Latency req. (command execution time) | Raw size of data prior to transmission (bytes) |  | Security | TCP/IP packet + overhead per packet (Data+ 50bytes) | TCP/IP data transmission overheads (data + 500) bytes | Cumulative per activity (bytes) | Data Flow per year
[9 empty] | Formula | Total | 22 | 50 | 500 |  | Bytes per year | Cumulative per year
Use Case 1 - Gather information for planning
1. The Smart Metering System sends the recorded gas demand data to the GDNO (6min) | 8 | Interval Gas values | 4 | Every 6 minutes all day for the winter period (Was November-March) - 6 months | SM | once a year | CCP | 5 days | 4x240x183 | 175200 | 175222 | 175272 | 175772 | 175772 | 175772 | 175772 |  | 171.6523
|  |  |  | Every 6 min. in summer (was June-September) all day for 6 months | SM | once a year | CCP | 5 days | 4x240x183 | 175200 | 175222 | 175272 | 175772 | 351544 | 175772 | 351544 |  | 343.3047
2. The Smart Metering System sends the recorded gas demand data to the GDNO (daily) |  | Daily Gas values | 4 | every day at 6 am | SM | every 6 months | CCP | 5 days | 4x183 | 730 | 752 | 802 | 1302 | 352846 | 2604 | 354148
Alternative Flow:
1. Meter does not communicate requested data to the authorised GDN party | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, GDN | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, GDN | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
2. Meter data reads are missing / corrupted | 296 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, GDN | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Request for weekly reads | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, GDN | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3700 | 597 | 3700
|  | Weekly read submission | 28 | on event (assumed once a year) | SM | once a year | CCP |  | 28x1 | 28 | 50 | 100 | 600 | 4300 | 600 | 4300
Use Case 02 - Configure Smart Metering System
1. GDN configures meter reading registers | 100 | GDN configure meter reading register | 25 | on event (assumed to happen every 3 years) | GDN | every 3 years | SM | confirmation almost real time | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Confirmation sent | 25 | on event (assumed ever 3 years) | SM | every 3 years | GDN |  | 25x1 | 25 | 47 | 97 | 597 | 1194 | 597 | 1194
|  | GDN configure meter alarms | 25 | on event (assumed to happen every 3 years) | GDN | every 3 years | SM | almost real time | 25 x 1 | 25 | 47 | 97 | 597 | 1791 | 597 | 1791
|  | Confirmation sent | 25 | on event (assumed ever 3 years) | SM | every 3 years | GDN |  | 25x1 | 25 | 47 | 97 | 597 | 2388 | 597 | 2388
Alternative Flow:
1. Smart Metering deems the request invalid | 43 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, GDN | 12 hours | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18 x 1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
2. GDNs do not receive confirmation | 243 | Failure notification | 25 | on occurrence (assumed to happen every 3 years) | SM | every 3 years | CCP,GDN | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on occurrence (assumed to happen every 3 years) | SM | every 3 years | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on occurrence (assumed to happen every 3 years) | CCP | every 3 years | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on occurrence (assumed to happen every 3 years) | SM | every 3 years | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed to happen every 3 years) | SM | every 3 years | CCP, GDN | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
Use Case 03 - Disable Supply of Gas
1. Gas is disabled by GDNs | 75 | GDN disables gas supply | 25 | on event (assumed once every 3 years) | GDN | every 3 years | SM | almost real time | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Meter sends confirmation | 25 | on event (assumed once every 3 years) | SM | every 3 years | GDN | almost real time | 25 x 1 | 25 | 47 | 97 | 597 | 1194 | 597 | 1194
|  | GDN enable gas supply | 25 | on event (assumed once every 3 years) | SM | every 3 years | GDN | almost real time | 25 x 1 | 25 | 47 | 97 | 597 | 1791 | 597 | 1791
Alternative Flow:
GDNs do not receive confirmation | 243 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, GDN | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on event (assumed once a year) | CCP | once a year | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on event (assumed once a year) | SM | once a year | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on event (assumed once a year) | SM | once a year | CCP, GDN | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
Smart Metering deems the request invalid | 43 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, GDN | 12 hours | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18 x 1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
Use Case 04 - Display Messages from Gas Distribution Network
GDN sends notification to IHD | 50 | GDN send message to IHD | 25 | on occurrence to happen once every 10 years | GDN | every 10 years | SM | almost real time | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | meter acknowledges | 25 | on occurrence to happen once every 10 years | SM | every 10 years | GDN | almost real time | 25 x 1 | 25 | 47 | 97 | 597 | 1194 | 597 | 1194
Alternative Flow:
Meter fails to send confirmation message | 243 | Failure notification | 25 | on occurrence | SM | on event | CCP, GDN | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on occurrence | SM | on event | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | Test request | 25 | on occurrence | CCP | on event | SM |  | 25x1 | 25 | 47 | 97 | 597 | 1784 | 597 | 1784
|  | Performance report | 150 | on occurrence | SM | on event | CCP |  | 150x1 | 150 | 172 | 222 | 722 | 2506 | 722 | 2506
|  | Service restored notification | 25 | on occurrence | SM | on event | CCP, GDN | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 3103 | 597 | 3103
Use Case 05 - Measure and Store Calorific Values at the meter
Update CV | 33 | CV value for the day | 8 | daily | GDN | daily | SM | almost real time | 8x1 | 8 | 30 | 80 | 580 | 580 | 211700 | 211700
|  | Confirmation | 25 | daily | SM | daily | GDN | almost real time | 25x1 | 25 | 47 | 97 | 597 | 1177 | 217905 | 429605
(Optionally) GDN update the message | 33 | Updated CV value for the day | 8 | on occurrence (assumed to happen once a month) | GDN | monthly | SM | almost real time | 8x1 | 8 | 30 | 80 | 580 | 580 | 6960 | 6960
|  | Confirmation | 25 | monthly | SM | monthly | GDN | almost real time | 25x1 | 25 | 47 | 97 | 597 | 1177 | 7164 | 14124
Alternative Flow:
1. The Smart Metering System rejects the message as invalid | 76 | Failure notification | 25 | on event (assumed once a year) | SM | once a year | CCP, GDN | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 597 | 597 | 597
|  | Error Report | 18 | on event (assumed once a year) | SM | once a year | CCP |  | 18x1 | 18 | 40 | 90 | 590 | 1187 | 590 | 1187
|  | GDN resends the message | 8 | on event (assumed once a year) | CCP | once a year | SM |  | 8x1 | 8 | 30 | 80 | 580 | 1767 | 580 | 1767
|  | Confirmation | 25 | on event (assumed once a year) | SM | once a year | CCP, GDN | 12 hours | 25x1 | 25 | 47 | 97 | 597 | 2364 | 597 | 2364
Tampering Notification send to GDNs
meter sends tampering notification to GDNs | 25 | Meter sends tampering notification | 25 | on occurrence (assumed once a year) | SM | once a year | GDN | almost real time | 25 x 1 | 25 | 47 | 97 | 597 | 597 | 597 | 597 | Per Meter |  | 20 | Million
TOTAL per meter - everything works well | [9 empty] | 351446 | 351820 | 352670 |  | 361170 |  | 803847 | 785.0068 | 0.76661 | 14972.8172 | 14.6219
TOTAL per meter - everything fails once | [9 empty] | 352876 | 354020 | 356620 |  | 382620 |  | 825297 | 805.9541 | 0.78706 | 15372.3545 | 15.0121
[14 empty] | 352.7051 | 0.34444 |  | kbytes | Mbytes | Gbytes | Tbytes
[14 empty] | 373.6523 | 0.36489
[14 empty] | kbytes | Mbytes |  |  | 1 | 19531.25 | 19.0735

## Ele_DataTrafficSpeed
Speed - bps (bits per second) is obtained by multiplying bytes by 8 to get bits and deviding by seconds needed for response time |  |  | Speed per packet depending on response time required (bps) | [7 empty] | Speed on cumulative volumes depending on response time required (bps)
| Type of data | TCP/IP data transmission overheads (data + 500) bytes | Response time required: 5sec | Response time required: 30 sec | Response time required: 3min | Response time required: 5min | Response time required: 15min | Response time required: 1 hour | Response time required: 12 hours | Cumulative per activity (bytes) | Response time required: 5sec | Response time required: 30 sec | Response time required: 3min | Response time required: 5min | Response time required: 15min | Response time required: 1 hour | Response time required: 12 hours
Assessment of network performance |  |  | 5 | 30 | 180 | 300 | 900 | 3600 | 43200 |  | 5 | 30 | 180 | 300 | 900 | 3600 | 43200
Use Case 01 - Monitor current flows and voltage levels to identify thermal capacity and statutory voltage headroom
1. Data is periodically sent from the Smart Metering System | Real Power (import) (kW) | 18236 | 29177.6 | 4862.9333 | 810.4889 | 486.2933 | 162.0978 | 40.5244 | 3.377 | 18236 | 29177.6 | 4862.9333 | 810.4889 | 486.2933 | 162.0978 | 40.5244 | 3.377
| Reactive Power (import) (kVAr) | 18236 | 29177.6 | 4862.9333 | 810.4889 | 486.2933 | 162.0978 | 40.5244 | 3.377 | 36472 | 58355.2 | 9725.8667 | 1620.9778 | 972.5867 | 324.1956 | 81.0489 | 6.7541
| Real Power (export) (kW) | 18236 | 29177.6 | 4862.9333 | 810.4889 | 486.2933 | 162.0978 | 40.5244 | 3.377 | 54708 | 87532.8 | 14588.8 | 2431.4667 | 1458.88 | 486.2933 | 121.5733 | 10.1311
| Reactive Energy (export) (kVAr) | 18236 | 29177.6 | 4862.9333 | 810.4889 | 486.2933 | 162.0978 | 40.5244 | 3.377 | 72944 | 116710.4 | 19451.7333 | 3241.9556 | 1945.1733 | 648.3911 | 162.0978 | 13.5081
| Micro-generation Real Power (kW) | 18236 | 29177.6 | 4862.9333 | 810.4889 | 486.2933 | 162.0978 | 40.5244 | 3.377 | 91180 | 145888 | 24314.6667 | 4052.4444 | 2431.4667 | 810.4889 | 202.6222 | 16.8852
| Micro-generation Reactive Power (kVAr) | 18236 | 29177.6 | 4862.9333 | 810.4889 | 486.2933 | 162.0978 | 40.5244 | 3.377 | 109416 | 175065.6 | 29177.6 | 4862.9333 | 2917.76 | 972.5867 | 243.1467 | 20.2622
| Voltage | 18236 | 29177.6 | 4862.9333 | 810.4889 | 486.2933 | 162.0978 | 40.5244 | 3.377 | 127652 | 204243.2 | 34040.5333 | 5673.4222 | 3404.0533 | 1134.6844 | 283.6711 | 23.6393
| Power Factor | 18236 | 29177.6 | 4862.9333 | 810.4889 | 486.2933 | 162.0978 | 40.5244 | 3.377 | 145888 | 233420.8 | 38903.4667 | 6483.9111 | 3890.3467 | 1296.7822 | 324.1956 | 27.0163
2. DNO requests data | Command to send data | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
3. The Smart Metering System sends the requested data | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | 40892 | 65427.2 | 10904.5333 | 1817.4222 | 1090.4533 | 363.4844 | 90.8711 | 7.5726 | 40892 | 65427.2 | 10904.5333 | 1817.4222 | 1090.4533 | 363.4844 | 90.8711 | 7.5726
Alternative Flow:
1. Smart Metering System rejects the message as invalid | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
2. The Smart Metering System does not have any measured data stored | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Request for weekly reads | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3700 | 5920 | 986.6667 | 164.4444 | 98.6667 | 32.8889 | 8.2222 | 0.68519
| Weekly read submission | 600 | 960 | 160 | 26.6667 | 16 | 5.3333 | 1.3333 | 0.11111 | 4300 | 6880 | 1146.6667 | 191.1111 | 114.6667 | 38.2222 | 9.5556 | 0.7963
3.1 The DNO does not receive the data from the Smart Metering System (scenario 1) | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
3.2 The DNO does not receive the data from the Smart Metering System (scenario 2) | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
Use Case 02 - Determine network impact of proposed new demand / generation connections
1. DNO requests stored HH power flow and voltage data (and micro-generation data where available) | Command to send data | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
2. Smart Metering System retrieves the requested data | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | 40892 | 65427.2 | 10904.5333 | 1817.4222 | 1090.4533 | 363.4844 | 90.8711 | 7.5726 | 41489 | 66382.4 | 11063.7333 | 1843.9556 | 1106.3733 | 368.7911 | 92.1978 | 7.6831
Alternative Flow:
1. The DNO does not receive the data | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
Use Case 03 - Determine network impact of proposed increase in demand / generation at existing connection points
1. DNO requests stored HH power flow and voltage data (and micro-generation data where available) | Command to send data | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
2. Smart Metering System retrieves the requested data | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | 40892 | 65427.2 | 10904.5333 | 1817.4222 | 1090.4533 | 363.4844 | 90.8711 | 7.5726 | 41489 | 66382.4 | 11063.7333 | 1843.9556 | 1106.3733 | 368.7911 | 92.1978 | 7.6831
Alternative Flow:
1. The DNO does not receive the data | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
Use Case 04 - Monitor demand and generation profiles for network load forecasting
1. At the defined interval the Smart Metering System collects the data and sends it to the DNO (please see Use Case 01 scenario 1 and alternate flow 4) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Use Case 05 - Determine Latent Demand due to Embedded Generation
1. At the defined interval the Smart Metering System collects the data and sends it to the DNO (please see Use Case 01 scenario 1 and alternate flow 4) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Use Case 06 - Identify Voltage Quality Issues
1. The Smart Metering System accumulates time and data stamped voltage quality events (assumed 6 events) | Meter sends event report | 656 | 1049.6 | 174.9333 | 29.1556 | 17.4933 | 5.8311 | 1.4578 | 0.12148 | 656 | 1049.6 | 174.9333 | 29.1556 | 17.4933 | 5.8311 | 1.4578 | 0.12148
Alternative Flow:
1. Meter fails to send the message | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
Actively manage network / System Balancing
Use Case 07 - Collect data for active management
1. Data is periodically sent from the Smart Metering System (import/export; real/reactive flow, real/reactive generation flow and voltage as specified by DNOs) as in Use Case 01 Scenario 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative Flow:
Meter fails to send the message | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
08 Use Case - Active network management of network voltage – Uses Voltage information captured to instigate actions on DNO Assets to control voltage, as well as having the same data flows as Use Case 09 to undertake actions in the household to address voltage issues via ToU/Peak tariffs, control household equipment etc.
The same data flow as in Use Case 09 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
09 Use Case - Perform Active Management of Network Power Flow
1. Operation of (Distribution Use of System) Time of Use tariff | TOU tariffs configured | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Notification of new TOU | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1194 | 1910.4 | 318.4 | 53.0667 | 31.84 | 10.6133 | 2.6533 | 0.22111
| TOU readings provided to DNO's (assumed summer tariff- daily reads for 60 days) | 812 | 1299.2 | 216.5333 | 36.0889 | 21.6533 | 7.2178 | 1.8044 | 0.15037 | 2006 | 3209.6 | 534.9333 | 89.1556 | 53.4933 | 17.8311 | 4.4578 | 0.37148
2. Operation of (Distribution Use of System) Real Time Pricing | Real time tariff notification sent | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Notification of new TOU | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1194 | 1910.4 | 318.4 | 53.0667 | 31.84 | 10.6133 | 2.6533 | 0.22111
3. Power Sharing by Maximum Thresholds | Notification of "load exceeded" sent | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Notification "load within acceptable limits" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4. Direct Control, by DNOs, of appliance or micro-generation | Command to control (disconnect) the appliance or disable supply | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Command to reconnect the appliance or enable the supply | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1194 | 1910.4 | 318.4 | 53.0667 | 31.84 | 10.6133 | 2.6533 | 0.22111
Alternative Flow:
1. Maximum Power Threshold Reached - consumer does not turn off appliances | Notification of "load exceeded" sent | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2. Power Sharing by Maximum Power Thresholds - consumer turns off some of the appliances | Notification of "load exceeded" sent | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Notification "load within acceptable limits" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
System Balancing
10 Use Case - Perform System Balancing
The same data flow as in Use Case 08 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 Use Case - Check effectiveness of active network management / system balancing measures
1. The Smart Metering System measures power flow and voltage data (as in Use Case 01 scenario 01) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2. DNO requests data | Command to send data | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
3. The Smart Metering System sends the requested data | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | 40892 | 65427.2 | 10904.5333 | 1817.4222 | 1090.4533 | 363.4844 | 90.8711 | 7.5726 | 41489 | 66382.4 | 11063.7333 | 1843.9556 | 1106.3733 | 368.7911 | 92.1978 | 7.6831
Alternative Flow:
1. Meter fails to send the message | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
Actively manage network during planned and unplanned Outage
Use Case 12 - Notify consumer of planned outage
1. Consumer notification of planned / emergency outage | Notification sent (10 days in advance) | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Notification sent (outage is due to begin- 1 hour before the event) | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1194 | 1910.4 | 318.4 | 53.0667 | 31.84 | 10.6133 | 2.6533 | 0.22111
2. Consumer notified that outage is over | Notification the outage is over | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
Alternative Flow:
1. Smart Metering System deems the request invalid for scenario 1 | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 2865.6 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
2. DNOs do not receive akcnowledgment message for scenario 1 | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
3. Smart Metering System deems the request invalid for scenario 2 | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
4. DNOs do not receive akcnowledgment message for scenario 2 | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
Use Case 13 - Query Meter Energisation Status to determine Outage Source and Location
1. False Outage Report (DNO checks meter energisation status: supply on) | Energisation status "supply on" submitted | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Request for switch status | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1194 | 1910.4 | 318.4 | 53.0667 | 31.84 | 10.6133 | 2.6533 | 0.22111
| Response | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1791 | 2865.6 | 477.6 | 79.6 | 47.76 | 15.92 | 3.98 | 0.33167
2. Confirmed network outage | Request for energisation status | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Energisation status "supply off" submitted | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1194 | 1910.4 | 318.4 | 53.0667 | 31.84 | 10.6133 | 2.6533 | 0.22111
Alternative Flow:
1. Smart Metering deems the request invalid (for scenario 1) | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
2. DNO does not receive the message (scenario 1) | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
Use Case 14 - Send Alarm to DNO during network outage
1. Outage alarm sent to the Distribution Network Operator | Outage alarm sent | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
Alternative Flow:
1. Smart Metering System is unable to send the outage alarm message | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
2. DNO does not receive notification | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
Use Case 15 - Verify restoration of supplies after outage
1. Meter notifies DNOs of power restoration | "Power restored" notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
Alternative Flow:
1. Smart Metering System fails to detect power restoration | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
2. DNO does not receive notification | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
Use Case 16 - Regulatory Reporting of outages
1. DNO requests stored outage information | Command to send data | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
2. Meter sends outage report | Outage report sent | 564 | 902.4 | 150.4 | 25.0667 | 15.04 | 5.0133 | 1.2533 | 0.10444 | 1161 | 1857.6 | 309.6 | 51.6 | 30.96 | 10.32 | 2.58 | 0.215
Alternative Flow:
1. Smart Metering rejects the message as invalid | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
2. Smart Metering System does not have any of the requested information stored | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Request for weekly reads | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3700 | 5920 | 986.6667 | 164.4444 | 98.6667 | 32.8889 | 8.2222 | 0.68519
| Weekly read submission | 600 | 960 | 160 | 26.6667 | 16 | 5.3333 | 1.3333 | 0.11111 | 4300 | 6880 | 1146.6667 | 191.1111 | 114.6667 | 38.2222 | 9.5556 | 0.7963
3. DNO does not receive notification | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
Use Case 17 - Restore and maintain supply during outages
1. Smart Metering System sends "power restored" message to the DNO | "Power restored" notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
2. DNO activates the maximum power consumption threshold | Command to active power threshold | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
3. Smart Metering confirms activation of the maximum power consumption threshold | Confirmation sent | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1194 | 1910.4 | 318.4 | 53.0667 | 31.84 | 10.6133 | 2.6533 | 0.22111
Alternative Flow:
1. DNO does not receive "power restored" message | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
2. Smart Metering deems the request invalid | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
3. DNO does not receive the confirmation response | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
Manage safety issues
Use Case 18 - Manage meter safety alarm
1. Smart Metering System sends alarm to DNOs | Alarm sent | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
2. DNO remotely disconnects the supply through the Smart Metering System (where necessary) | Disconnection command | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1194 | 1910.4 | 318.4 | 53.0667 | 31.84 | 10.6133 | 2.6533 | 0.22111
3. The Smart Metering sends the confirmation message to the DNO | Confirmation sent | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1791 | 2865.6 | 477.6 | 79.6 | 47.76 | 15.92 | 3.98 | 0.33167
Alternative Flow: |  |  | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
1. DNO does not receive the alarm | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
2. Smart Metering deems the request invalid | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
3. DNO does not receive confirmation of the supply switch activating to cut-off supply | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
Use Case 19 - Manage extreme voltage at meter
1. The Smart Metering System sends alarm of a voltage level outside its ocnfigured tolerance levels | Alarm sent | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
2. (Optionally) the Smart Metering System auto-disconnects itself from the network supply of electricity sending confirmation of disconnection to the DNO | Supply disabled | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1194 | 1910.4 | 318.4 | 53.0667 | 31.84 | 10.6133 | 2.6533 | 0.22111
3. Supply is enabled by DNO after emergency/safety action | Supply enabled | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1791 | 2865.6 | 477.6 | 79.6 | 47.76 | 15.92 | 3.98 | 0.33167
Alternative Flow:
1. The Smart Metering System fails to send the extreme voltage alarm | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
2. The Smart Metering System fails to auto disconnect | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
Support network activities
Use Case 20 - Configure Smart Metering System
1. DNO configures meter reading registers | DNO configures meter reading register | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Confirmation sent | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1194 | 1910.4 | 318.4 | 53.0667 | 31.84 | 10.6133 | 2.6533 | 0.22111
2. DNO configures meter alarms | DNO configures meter alarms | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Confirmation sent | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1194 | 1910.4 | 318.4 | 53.0667 | 31.84 | 10.6133 | 2.6533 | 0.22111
3. DNO configures meter load threshold | DNO configures load threshold | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Confirmation sent | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1194 | 1910.4 | 318.4 | 53.0667 | 31.84 | 10.6133 | 2.6533 | 0.22111
Alternative Flow:
1. Smart Metering deems the request invalid | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
2. DNOs do not receive notification | Failure notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056
| Error Report | 590 | 944 | 157.3333 | 26.2222 | 15.7333 | 5.2444 | 1.3111 | 0.10926 | 1187 | 1899.2 | 316.5333 | 52.7556 | 31.6533 | 10.5511 | 2.6378 | 0.21981
| Test request | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 1784 | 2854.4 | 475.7333 | 79.2889 | 47.5733 | 15.8578 | 3.9644 | 0.33037
| Performance report | 722 | 1155.2 | 192.5333 | 32.0889 | 19.2533 | 6.4178 | 1.6044 | 0.1337 | 2506 | 4009.6 | 668.2667 | 111.3778 | 66.8267 | 22.2756 | 5.5689 | 0.46407
| Service restored notification | 597 | 955.2 | 159.2 | 26.5333 | 15.92 | 5.3067 | 1.3267 | 0.11056 | 3103 | 4964.8 | 827.4667 | 137.9111 | 82.7467 | 27.5822 | 6.8956 | 0.57463
TOTAL per meter - everything works well |  | 332980 | 532768 | 88794.6667 | 14799.1111 | 8879.4667 | 2959.8222 | 739.9556 | 61.663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL per meter - everything fails once |  | 419342 | 670947.2 | 111824.5333 | 18637.4222 | 11182.4533 | 3727.4844 | 931.8711 | 124.2495 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Gas_DataTrafficSpeed
Speed - bps (bits per second) is obtained by multiplying bytes by 8 to get bits and deviding by seconds needed for response time |  |  | Speed per packet depending on respoonse time required (bps) |  |  |  | Speed on cumulative volumes depending on respoonse time required (bps)
| Type of data | TCP/IP data transmission overheads (data + 500) bytes | Response time required: 5sec (min) | Response time required: 15min | Response time required: 1 hour | Cumulative per activity (bytes) | Response time required: 5sec (min) | Response time required: 15min | Response time required: 1 hour
|  | 500 | 5 | 900 | 3600 |  | 5 | 900 | 3600
Use Case 1 - Gather information for planning
1. The Smart Metering System sends the recorded gas demand data to the GDNO (6min) | Interval Gas values | 175772 | 281235.2 | 1562.4178 | 390.6044 | 175772 | 281235.2 | 1562.4178 | 390.6044
|  | 175772 | 281235.2 | 1562.4178 | 390.6044 | 351544 | 562470.4 | 3124.8356 | 781.2089
2. The Smart Metering System sends the recorded gas demand data to the GDNO (daily) | Daily Gas values | 1302 | 2083.2 | 11.5733 | 2.8933 | 352846 | 564553.6 | 3136.4089 | 784.1022
Alternative Flow:
1. Meter does not communicate requested data to the authorised GDN party | Failure notification | 597 | 955.2 | 5.3067 | 1.3267 | 597 | 955.2 | 5.3067 | 1.3267
| Error Report | 590 | 944 | 5.2444 | 1.3111 | 1187 | 1899.2 | 10.5511 | 2.6378
| Test request | 597 | 955.2 | 5.3067 | 1.3267 | 1784 | 2854.4 | 15.8578 | 3.9644
| Performance report | 722 | 1155.2 | 6.4178 | 1.6044 | 2506 | 4009.6 | 22.2756 | 5.5689
| Service restored notification | 597 | 955.2 | 5.3067 | 1.3267 | 3103 | 4964.8 | 27.5822 | 6.8956
2. Meter data reads are missing / corrupted | Failure notification | 597 | 955.2 | 5.3067 | 1.3267 | 597 | 955.2 | 5.3067 | 1.3267
| Error Report | 590 | 944 | 5.2444 | 1.3111 | 1187 | 1899.2 | 10.5511 | 2.6378
| Test request | 597 | 955.2 | 5.3067 | 1.3267 | 1784 | 2854.4 | 15.8578 | 3.9644
| Performance report | 722 | 1155.2 | 6.4178 | 1.6044 | 2506 | 4009.6 | 22.2756 | 5.5689
| Request for weekly reads | 597 | 955.2 | 5.3067 | 1.3267 | 3103 | 4964.8 | 27.5822 | 6.8956
| Service restored notification | 597 | 955.2 | 5.3067 | 1.3267 | 3700 | 5920 | 32.8889 | 8.2222
| Weekly read submission | 600 | 960 | 5.3333 | 1.3333 | 4300 | 6880 | 38.2222 | 9.5556
Use Case 02 - Configure Smart Metering System
1. GDN configures meter reading registers | GDN configure meter reading register | 597 | 955.2 | 5.3067 | 1.3267 | 597 | 955.2 | 5.3067 | 1.3267
| Confirmation sent | 597 | 955.2 | 5.3067 | 1.3267 | 1194 | 1910.4 | 10.6133 | 2.6533
| GDN configure meter alarms | 597 | 955.2 | 5.3067 | 1.3267 | 1791 | 2865.6 | 15.92 | 3.98
| Confirmation sent | 597 | 955.2 | 5.3067 | 1.3267 | 2388 | 3820.8 | 21.2267 | 5.3067
Alternative Flow:
1. Smart Metering deems the request invalid | Failure notification | 597 | 955.2 | 5.3067 | 1.3267 | 597 | 955.2 | 5.3067 | 1.3267
| Error Report | 590 | 944 | 5.2444 | 1.3111 | 1187 | 1899.2 | 10.5511 | 2.6378
2. GDNs do not receive confirmation | Failure notification | 597 | 955.2 | 5.3067 | 1.3267 | 597 | 955.2 | 5.3067 | 1.3267
| Error Report | 590 | 944 | 5.2444 | 1.3111 | 1187 | 1899.2 | 10.5511 | 2.6378
| Test request | 597 | 955.2 | 5.3067 | 1.3267 | 1784 | 2854.4 | 15.8578 | 3.9644
| Performance report | 722 | 1155.2 | 6.4178 | 1.6044 | 2506 | 4009.6 | 22.2756 | 5.5689
| Service restored notification | 597 | 955.2 | 5.3067 | 1.3267 | 3103 | 4964.8 | 27.5822 | 6.8956
Use Case 03 - Disable Supply of Gas
1. Gas is disabled by GDNs | GDN disables gas supply | 597 | 955.2 | 5.3067 | 1.3267 | 597 | 955.2 | 5.3067 | 1.3267
| Meter sends confirmation | 597 | 955.2 | 5.3067 | 1.3267 | 1194 | 1910.4 | 10.6133 | 2.6533
| GDN enable gas supply | 597 | 955.2 | 5.3067 | 1.3267 | 1791 | 2865.6 | 15.92 | 3.98
Alternative Flow:
GDNs do not receive confirmation | Failure notification | 597 | 955.2 | 5.3067 | 1.3267 | 597 | 955.2 | 5.3067 | 1.3267
| Error Report | 590 | 944 | 5.2444 | 1.3111 | 1187 | 1899.2 | 10.5511 | 2.6378
| Test request | 597 | 955.2 | 5.3067 | 1.3267 | 1784 | 2854.4 | 15.8578 | 3.9644
| Performance report | 722 | 1155.2 | 6.4178 | 1.6044 | 2506 | 4009.6 | 22.2756 | 5.5689
| Service restored notification | 597 | 955.2 | 5.3067 | 1.3267 | 3103 | 4964.8 | 27.5822 | 6.8956
Smart Metering deems the request invalid | Failure notification | 597 | 955.2 | 5.3067 | 1.3267 | 597 | 955.2 | 5.3067 | 1.3267
| Error Report | 590 | 944 | 5.2444 | 1.3111 | 1187 | 1899.2 | 10.5511 | 2.6378
Use Case 04 - Display Messages from Gas Distribution Network
GDN sends notification to IHD | GDN send message to IHD | 597 | 955.2 | 5.3067 | 1.3267 | 597 | 955.2 | 5.3067 | 1.3267
| meter acknowledges | 597 | 955.2 | 5.3067 | 1.3267 | 1194 | 1910.4 | 10.6133 | 2.6533
Alternative Flow:
Meter fails to send confirmation message | Failure notification | 597 | 955.2 | 5.3067 | 1.3267 | 597 | 955.2 | 5.3067 | 1.3267
| Error Report | 590 | 944 | 5.2444 | 1.3111 | 1187 | 1899.2 | 10.5511 | 2.6378
| Test request | 597 | 955.2 | 5.3067 | 1.3267 | 1784 | 2854.4 | 15.8578 | 3.9644
| Performance report | 722 | 1155.2 | 6.4178 | 1.6044 | 2506 | 4009.6 | 22.2756 | 5.5689
| Service restored notification | 597 | 955.2 | 5.3067 | 1.3267 | 3103 | 4964.8 | 27.5822 | 6.8956
Use Case 05 - Measure and Store Calorific Values at the meter
| CV value for the day | 580 | 928 | 5.1556 | 1.2889 | 580 | 928 | 5.1556 | 1.2889
| Confirmation | 597 | 955.2 | 5.3067 | 1.3267 | 1177 | 1883.2 | 10.4622 | 2.6156
(Optionally) GDN update the message | CV value for the day | 580 | 928 | 5.1556 | 1.2889 | 580 | 928 | 5.1556 | 1.2889
| Confirmation | 597 | 955.2 | 5.3067 | 1.3267 | 1177 | 1883.2 | 10.4622 | 2.6156
Alternative Flow:
1. The Smart Metering System rejects the message as invalid | Failure notification | 597 | 955.2 | 5.3067 | 1.3267 | 597 | 955.2 | 5.3067 | 1.3267
| Error Report | 590 | 944 | 5.2444 | 1.3111 | 1187 | 1899.2 | 10.5511 | 2.6378
| GDN resends the message | 580 | 928 | 5.1556 | 1.2889 | 1767 | 2827.2 | 15.7067 | 3.9267
| Confirmation | 597 | 955.2 | 5.3067 | 1.3267 | 2364 | 3782.4 | 21.0133 | 5.2533
Tampering Notification send to GDNs
| Meter sends tampering notification | 597 | 955.2 | 5.3067 | 1.3267 | 597 | 955.2 | 5.3067 | 1.3267
TOTAL per meter - everything works well | [5 empty] | 361170 | 577872 | 3210.4 | 802.6
TOTAL per meter - everything fails once | [5 empty] | 382620 | 612192 | 3401.0667 | 850.2667

## Ele_DataSpeedMultpMeters
Speed - bps (bits per second) is obtained by multiplying bytes by 8 to get bits and deviding by seconds needed for response time |  |  |  |  | Speed per packet depending on response time required (bps) | [7 empty] | Speed on cumulative volumes depending on response time required (bps)
| Type of data | TCP/IP data transmission overheads (data + 500) bytes |  | 1,000 Meters Simultaniously | Response time required: 5sec | Response time required: 30 sec | Response time required: 3min | Response time required: 5min | Response time required: 15min | Response time required: 1 hour | Response time required: 12 hours | Cumulative per activity (bytes) | Response time required: 5sec | Response time required: 30 sec | Response time required: 3min | Response time required: 5min | Response time required: 15min | Response time required: 1 hour | Response time required: 12 hours
Assessment of network performance |  |  |  | 1000 | 5 | 30 | 180 | 300 | 900 | 3600 | 43200 |  | 5 | 30 | 180 | 300 | 900 | 3600 | 43200
Use Case 01 - Monitor current flows and voltage levels to identify thermal capacity and statutory voltage headroom
1. Data is periodically sent from the Smart Metering System | Real Power (import) (kW) | 18236 | 1000 | 18236000 | 29177600 | 4862933.3333 | 810488.8889 | 486293.3333 | 162097.7778 | 40524.4444 | 3377.037 | 18236000 | 29177600 | 4862933.3333 | 810488.8889 | 486293.3333 | 162097.7778 | 40524.4444 | 3377.037
| Reactive Power (import) (kVAr) | 18236 | 1000 | 18236000 | 29177600 | 4862933.3333 | 810488.8889 | 486293.3333 | 162097.7778 | 40524.4444 | 3377.037 | 36472000 | 58355200 | 9725866.6667 | 1620977.7778 | 972586.6667 | 324195.5556 | 81048.8889 | 6754.0741
| Real Power (export) (kW) | 18236 | 1000 | 18236000 | 29177600 | 4862933.3333 | 810488.8889 | 486293.3333 | 162097.7778 | 40524.4444 | 3377.037 | 54708000 | 87532800 | 14588800 | 2431466.6667 | 1458880 | 486293.3333 | 121573.3333 | 10131.1111
| Reactive Energy (export) (kVAr) | 18236 | 1000 | 18236000 | 29177600 | 4862933.3333 | 810488.8889 | 486293.3333 | 162097.7778 | 40524.4444 | 3377.037 | 72944000 | 116710400 | 19451733.3333 | 3241955.5556 | 1945173.3333 | 648391.1111 | 162097.7778 | 13508.1481
| Micro-generation Real Power (kW) | 18236 | 1000 | 18236000 | 29177600 | 4862933.3333 | 810488.8889 | 486293.3333 | 162097.7778 | 40524.4444 | 3377.037 | 91180000 | 145888000 | 24314666.6667 | 4052444.4444 | 2431466.6667 | 810488.8889 | 202622.2222 | 16885.1852
| Micro-generation Reactive Power (kVAr) | 18236 | 1000 | 18236000 | 29177600 | 4862933.3333 | 810488.8889 | 486293.3333 | 162097.7778 | 40524.4444 | 3377.037 | 109416000 | 175065600 | 29177600 | 4862933.3333 | 2917760 | 972586.6667 | 243146.6667 | 20262.2222
| Voltage | 18236 | 1000 | 18236000 | 29177600 | 4862933.3333 | 810488.8889 | 486293.3333 | 162097.7778 | 40524.4444 | 3377.037 | 127652000 | 204243200 | 34040533.3333 | 5673422.2222 | 3404053.3333 | 1134684.4444 | 283671.1111 | 23639.2593
| Power Factor | 18236 | 1000 | 18236000 | 29177600 | 4862933.3333 | 810488.8889 | 486293.3333 | 162097.7778 | 40524.4444 | 3377.037 | 145888000 | 233420800 | 38903466.6667 | 6483911.1111 | 3890346.6667 | 1296782.2222 | 324195.5556 | 27016.2963
2. DNO requests data | Command to send data | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 146485000 | 234376000 | 39062666.6667 | 6510444.4444 | 3906266.6667 | 1302088.8889 | 325522.2222 | 27126.8519
3. The Smart Metering System sends the requested data | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | 40892 | 1000 | 40892000 | 65427200 | 10904533.3333 | 1817422.2222 | 1090453.3333 | 363484.4444 | 90871.1111 | 7572.5926 | 187377000 | 299803200 | 49967200 | 8327866.6667 | 4996720 | 1665573.3333 | 416393.3333 | 34699.4444
Alternative Flow: |  |  |  |  | 233420800 | 38903466.6667 | 6483911.1111 | 3890346.6667 | 1296782.2222 | 324195.5556 | 27016.2963
1. Smart Metering System rejects the message as invalid | Failure notification | 597 | 1000 | 597000 | 30132800 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
2. The Smart Metering System does not have any measured data stored | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Request for weekly reads | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3700000 | 5920000 | 986666.6667 | 164444.4444 | 98666.6667 | 32888.8889 | 8222.2222 | 685.1852
| Weekly read submission | 600 | 1000 | 600000 | 960000 | 160000 | 26666.6667 | 16000 | 5333.3333 | 1333.3333 | 111.1111 | 4300000 | 6880000 | 1146666.6667 | 191111.1111 | 114666.6667 | 38222.2222 | 9555.5556 | 796.2963
3.1 The DNO does not receive the data from the Smart Metering System (scenario 1) | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
3.2 The DNO does not receive the data from the Smart Metering System (scenario 2) | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
Use Case 02 - Determine network impact of proposed new demand / generation connections
1. DNO requests stored HH power flow and voltage data (and micro-generation data where available) | Command to send data | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
2. Smart Metering System retrieves the requested data | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | 40892 | 1000 | 40892000 | 65427200 | 10904533.3333 | 1817422.2222 | 1090453.3333 | 363484.4444 | 90871.1111 | 7572.5926 | 41489000 | 66382400 | 11063733.3333 | 1843955.5556 | 1106373.3333 | 368791.1111 | 92197.7778 | 7683.1481
Alternative Flow:
1. The DNO does not receive the data | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
Use Case 03 - Determine network impact of proposed increase in demand / generation at existing connection points
1. DNO requests stored HH power flow and voltage data (and micro-generation data where available) | Command to send data | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
2. Smart Metering System retrieves the requested data | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | 40892 | 1000 | 40892000 | 65427200 | 10904533.3333 | 1817422.2222 | 1090453.3333 | 363484.4444 | 90871.1111 | 7572.5926 | 41489000 | 66382400 | 11063733.3333 | 1843955.5556 | 1106373.3333 | 368791.1111 | 92197.7778 | 7683.1481
Alternative Flow:
1. The DNO does not receive the data | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
Use Case 04 - Monitor demand and generation profiles for network load forecasting
1. At the defined interval the Smart Metering System collects the data and sends it to the DNO (please see Use Case 01 scenario 1 and alternate flow 4) |  | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Use Case 05 - Determine Latent Demand due to Embedded Generation
1. At the defined interval the Smart Metering System collects the data and sends it to the DNO (please see Use Case 01 scenario 1 and alternate flow 4) |  | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Use Case 06 - Identify Voltage Quality Issues
1. The Smart Metering System accumulates time and data stamped voltage quality events (assumed 6 events) | Meter sends event report | 656 | 1000 | 656000 | 1049600 | 174933.3333 | 29155.5556 | 17493.3333 | 5831.1111 | 1457.7778 | 121.4815 | 656000 | 1049600 | 174933.3333 | 29155.5556 | 17493.3333 | 5831.1111 | 1457.7778 | 121.4815
Alternative Flow:
1. Meter fails to send the message | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
Actively manage network / System Balancing
Use Case 07 - Collect data for active management
1. Data is periodically sent from the Smart Metering System (import/export; real/reactive flow, real/reactive generation flow and voltage as specified by DNOs) as in Use Case 01 Scenario 1 |  | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative Flow:
Meter fails to send the message | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
08 Use Case - Active network management of network voltage – Uses Voltage information captured to instigate actions on DNO Assets to control voltage, as well as having the same data flows as Use Case 09 to undertake actions in the household to address voltage issues via ToU/Peak tariffs, control household equipment etc.
The same data flow as in Use Case 09 |  | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
09 Use Case - Perform Active Management of Network Power Flow
1. Operation of (Distribution Use of System) Time of Use tariff | TOU tariffs configured | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Notification of new TOU | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1194000 | 1910400 | 318400 | 53066.6667 | 31840 | 10613.3333 | 2653.3333 | 221.1111
| TOU readings provided to DNO's (assumed summer tariff- daily reads for 60 days) | 812 | 1000 | 812000 | 1299200 | 216533.3333 | 36088.8889 | 21653.3333 | 7217.7778 | 1804.4444 | 150.3704 | 2006000 | 3209600 | 534933.3333 | 89155.5556 | 53493.3333 | 17831.1111 | 4457.7778 | 371.4815
2. Operation of (Distribution Use of System) Real Time Pricing | Real time tariff notification sent | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Notification of new TOU | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1194000 | 1910400 | 318400 | 53066.6667 | 31840 | 10613.3333 | 2653.3333 | 221.1111
3. Power Sharing by Maximum Thresholds | Notification of "load exceeded" sent | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Notification "load within acceptable limits" | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4. Direct Control, by DNOs, of appliance or micro-generation | Command to control (disconnect) the appliance or disable supply | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Command to reconnect the appliance or enable the supply | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1194000 | 1910400 | 318400 | 53066.6667 | 31840 | 10613.3333 | 2653.3333 | 221.1111
Alternative Flow:
1. Maximum Power Threshold Reached - consumer does not turn off appliances | Notification of "load exceeded" sent | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2. Power Sharing by Maximum Power Thresholds - consumer turns off some of the appliances | Notification of "load exceeded" sent | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Notification "load within acceptable limits" | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
System Balancing
10 Use Case - Perform System Balancing
The same data flow as in Use Case 09 |  | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 Use Case - Check effectiveness of active network management / system balancing measures
1. The Smart Metering System measures power flow and voltage data (as in Use Case 01 scenario 01) |  | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2. DNO requests data | Command to send data | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
3. The Smart Metering System sends the requested data | Meter sends one month worth of HH real/reactive import/export, microgeneration real/reactive and voltage data | 40892 | 1000 | 40892000 | 65427200 | 10904533.3333 | 1817422.2222 | 1090453.3333 | 363484.4444 | 90871.1111 | 7572.5926 | 41489000 | 66382400 | 11063733.3333 | 1843955.5556 | 1106373.3333 | 368791.1111 | 92197.7778 | 7683.1481
Alternative Flow:
1. Meter fails to send the message | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
Actively manage network during planned and unplanned Outage
Use Case 12 - Notify consumer of planned outage
1. Consumer notification of planned / emergency outage | Notification sent (10 days in advance) | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Notification sent (outage is due to begin- 1 hour before the event) | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1194000 | 1910400 | 318400 | 53066.6667 | 31840 | 10613.3333 | 2653.3333 | 221.1111
2. Consumer notified that outage is over | Notification the outage is over | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1791000 | 2865600 | 477600 | 79600 | 47760 | 15920 | 3980 | 331.6667
Alternative Flow:
1. Smart Metering System deems the request invalid for scenario 1 | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
2. DNOs do not receive akcnowledgment message for scenario 1 | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
3. Smart Metering System deems the request invalid for scenario 2 | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
4. DNOs do not receive akcnowledgment message for scenario 2 | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
Use Case 13 - Query Meter Energisation Status to determine Outage Source and Location
1. False Outage Report (DNO checks meter energisation status: supply on) | Energisation status "supply on" submitted | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Request for switch status | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1194000 | 1910400 | 318400 | 53066.6667 | 31840 | 10613.3333 | 2653.3333 | 221.1111
| Response | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1791000 | 2865600 | 477600 | 79600 | 47760 | 15920 | 3980 | 331.6667
2. Confirmed network outage | Request for energisation status | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Energisation status "supply off" submitted | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1194000 | 1910400 | 318400 | 53066.6667 | 31840 | 10613.3333 | 2653.3333 | 221.1111
Alternative Flow:
1. Smart Metering deems the request invalid (for scenario 1) | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
2. DNO does not receive the message (scenario 1) | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
Use Case 14 - Send Alarm to DNO during network outage
1. Outage alarm sent to the Distribution Network Operator | Outage alarm sent | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
Alternative Flow:
1. Smart Metering System is unable to send the outage alarm message | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
2. DNO does not receive notification | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
Use Case 15 - Verify restoration of supplies after outage
1. Meter notifies DNOs of power restoration | "Power restored" notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
Alternative Flow:
1. Smart Metering System fails to detect power restoration | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
2. DNO does not receive notification | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
Use Case 16 - Regulatory Reporting of outages
1. DNO requests stored outage information | Command to send data | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
2. Meter sends outage report | Outage report sent | 564 | 1000 | 564000 | 902400 | 150400 | 25066.6667 | 15040 | 5013.3333 | 1253.3333 | 104.4444 | 1161000 | 1857600 | 309600 | 51600 | 30960 | 10320 | 2580 | 215
Alternative Flow:
1. Smart Metering rejects the message as invalid | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
2. Smart Metering System does not have any of the requested information stored | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Request for weekly reads | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3700000 | 5920000 | 986666.6667 | 164444.4444 | 98666.6667 | 32888.8889 | 8222.2222 | 685.1852
| Weekly read submission | 600 | 1000 | 600000 | 960000 | 160000 | 26666.6667 | 16000 | 5333.3333 | 1333.3333 | 111.1111 | 4300000 | 6880000 | 1146666.6667 | 191111.1111 | 114666.6667 | 38222.2222 | 9555.5556 | 796.2963
3. DNO does not receive notification | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
Use Case 17 - Restore and maintain supply during outages
1. Smart Metering System sends "power restored" message to the DNO | "Power restored" notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
2. DNO activates the maximum power consumption threshold | Command to active power threshold | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
3. Smart Metering confirms activation of the maximum power consumption threshold | Confirmation sent | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1194000 | 1910400 | 318400 | 53066.6667 | 31840 | 10613.3333 | 2653.3333 | 221.1111
Alternative Flow: |  |  |  |  | 2865600 | 477600 | 79600 | 47760 | 15920 | 3980 | 331.6667
1. DNO does not receive "power restored" message | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
2. Smart Metering deems the request invalid | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
3. DNO does not receive the confirmation response | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
Manage safety issues
Use Case 18 - Manage meter safety alarm
1. Smart Metering System sends alarm to DNOs | Alarm sent | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
2. DNO remotely disconnects the supply through the Smart Metering System (where necessary) | Disconnection command | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1194000 | 1910400 | 318400 | 53066.6667 | 31840 | 10613.3333 | 2653.3333 | 221.1111
3. The Smart Metering sends the confirmation message to the DNO | Confirmation sent | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1791000 | 2865600 | 477600 | 79600 | 47760 | 15920 | 3980 | 331.6667
Alternative Flow:
1. DNO does not receive the alarm | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
2. Smart Metering deems the request invalid | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
3. DNO does not receive confirmation of the supply switch activating to cut-off supply | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
Use Case 19 - Manage extreme voltage at meter
1. The Smart Metering System sends alarm of a voltage level outside its ocnfigured tolerance levels | Alarm sent | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
2. (Optionally) the Smart Metering System auto-disconnects itself from the network supply of electricity sending confirmation of disconnection to the DNO | Supply disabled | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1194000 | 1910400 | 318400 | 53066.6667 | 31840 | 10613.3333 | 2653.3333 | 221.1111
3. Supply is enabled by DNO after emergency/safety action | Supply enabled | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1791000 | 2865600 | 477600 | 79600 | 47760 | 15920 | 3980 | 331.6667
Alternative Flow:
1. The Smart Metering System fails to send the extreme voltage alarm | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
2. The Smart Metering System fails to auto disconnect | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
Support network activities
Use Case 20 - Configure Smart Metering System
1. DNO configures meter reading registers | DNO configures meter reading register | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Confirmation sent | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1194000 | 1910400 | 318400 | 53066.6667 | 31840 | 10613.3333 | 2653.3333 | 221.1111
2. DNO configures meter alarms | DNO configures meter alarms | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Confirmation sent | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1194000 | 1910400 | 318400 | 53066.6667 | 31840 | 10613.3333 | 2653.3333 | 221.1111
3. DNO configures meter load threshold | DNO configures load threshold | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Confirmation sent | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1194000 | 1910400 | 318400 | 53066.6667 | 31840 | 10613.3333 | 2653.3333 | 221.1111
Alternative Flow:
1. Smart Metering deems the request invalid | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
2. DNOs do not receive notification | Failure notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556
| Error Report | 590 | 1000 | 590000 | 944000 | 157333.3333 | 26222.2222 | 15733.3333 | 5244.4444 | 1311.1111 | 109.2593 | 1187000 | 1899200 | 316533.3333 | 52755.5556 | 31653.3333 | 10551.1111 | 2637.7778 | 219.8148
| Test request | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 1784000 | 2854400 | 475733.3333 | 79288.8889 | 47573.3333 | 15857.7778 | 3964.4444 | 330.3704
| Performance report | 722 | 1000 | 722000 | 1155200 | 192533.3333 | 32088.8889 | 19253.3333 | 6417.7778 | 1604.4444 | 133.7037 | 2506000 | 4009600 | 668266.6667 | 111377.7778 | 66826.6667 | 22275.5556 | 5568.8889 | 464.0741
| Service restored notification | 597 | 1000 | 597000 | 955200 | 159200 | 26533.3333 | 15920 | 5306.6667 | 1326.6667 | 110.5556 | 3103000 | 4964800 | 827466.6667 | 137911.1111 | 82746.6667 | 27582.2222 | 6895.5556 | 574.6296
TOTAL per meter - everything works well |  | 332980 |  | #REF! | 532768 | 88794.6667 | 14799.1111 | 8879.4667 | 2959.8222 | 739.9556 | 61.663 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL per meter - everything fails once |  | 419342 |  | 419342000 | 670947.2 | 111824.5333 | 18637.4222 | 11182.4533 | 3727.4844 | 931.8711 | 124.2495 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Gas_DataSpeedMultpMeters
Speed - bps (bits per second) is obtained by multiplying bytes by 8 to get bits and deviding by seconds needed for response time |  |  |  |  | Speed per packet depending on respoonse time required (bps) |  |  |  | Speed on cumulative volumes depending on respoonse time required (bps)
| Type of data | TCP/IP data transmission overheads (data + 500) bytes |  | 1,000 Meters Simultaniously | Response time required: 5sec | Response time required: 15min | Response time required: 1 hour | Cumulative per activity (bytes) | Response time required: 5sec | Response time required: 15min | Response time required: 1 hour
|  | 500 |  | 1000 | 5 | 900 | 3600 |  | 5 | 900 | 3600
Use Case 1 - Gather information for planning
1. The Smart Metering System sends the recorded gas demand data to the GDNO (6min) | Interval Gas values | 175772 | 1000 | 175772000 | 281235200 | 1562417.7778 | 390604.4444 | 175772000 | 281235200 | 1562417.7778 | 390604.4444
|  | 175772 | 1000 | 175772000 | 281235200 | 1562417.7778 | 390604.4444 | 351544000 | 562470400 | 3124835.5556 | 781208.8889
2. The Smart Metering System sends the recorded gas demand data to the GDNO (daily) | Daily Gas values | 1302 | 1000 | 1302000 | 2083200 | 11573.3333 | 2893.3333 | 352846000 | 564553600 | 3136408.8889 | 784102.2222
Alternative Flow:
1. Meter does not communicate requested data to the authorised GDN party | Failure notification | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 597000 | 955200 | 5306.6667 | 1326.6667
| Error Report | 590 | 1000 | 590000 | 944000 | 5244.4444 | 1311.1111 | 1187000 | 1899200 | 10551.1111 | 2637.7778
| Test request | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 1784000 | 2854400 | 15857.7778 | 3964.4444
| Performance report | 722 | 1000 | 722000 | 1155200 | 6417.7778 | 1604.4444 | 2506000 | 4009600 | 22275.5556 | 5568.8889
| Service restored notification | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 3103000 | 4964800 | 27582.2222 | 6895.5556
2. Meter data reads are missing / corrupted | Failure notification | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 597000 | 955200 | 5306.6667 | 1326.6667
| Error Report | 590 | 1000 | 590000 | 944000 | 5244.4444 | 1311.1111 | 1187000 | 1899200 | 10551.1111 | 2637.7778
| Test request | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 1784000 | 2854400 | 15857.7778 | 3964.4444
| Performance report | 722 | 1000 | 722000 | 1155200 | 6417.7778 | 1604.4444 | 2506000 | 4009600 | 22275.5556 | 5568.8889
| Request for weekly reads | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 3103000 | 4964800 | 27582.2222 | 6895.5556
| Service restored notification | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 3700000 | 5920000 | 32888.8889 | 8222.2222
| Weekly read submission | 600 | 1000 | 600000 | 960000 | 5333.3333 | 1333.3333 | 4300000 | 6880000 | 38222.2222 | 9555.5556
Use Case 02 - Configure Smart Metering System
1. GDN configures meter reading registers | GDN configure meter reading register | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 597000 | 955200 | 5306.6667 | 1326.6667
| Confirmation sent | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 1194000 | 1910400 | 10613.3333 | 2653.3333
| GDN configure meter alarms | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 1791000 | 2865600 | 15920 | 3980
| Confirmation sent | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 1194000 | 1910400 | 10613.3333 | 2653.3333
Alternative Flow:
1. Smart Metering deems the request invalid | Failure notification | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 597000 | 955200 | 5306.6667 | 1326.6667
| Error Report | 590 | 1000 | 590000 | 944000 | 5244.4444 | 1311.1111 | 1187000 | 1899200 | 10551.1111 | 2637.7778
2. GDNs do not receive confirmation | Failure notification | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 597000 | 955200 | 5306.6667 | 1326.6667
| Error Report | 590 | 1000 | 590000 | 944000 | 5244.4444 | 1311.1111 | 1187000 | 1899200 | 10551.1111 | 2637.7778
| Test request | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 1784000 | 2854400 | 15857.7778 | 3964.4444
| Performance report | 722 | 1000 | 722000 | 1155200 | 6417.7778 | 1604.4444 | 2506000 | 4009600 | 22275.5556 | 5568.8889
| Service restored notification | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 3103000 | 4964800 | 27582.2222 | 6895.5556
Use Case 03 - Disable Supply of Gas
1. Gas is disabled by GDNs | GDN disables gas supply | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 597000 | 955200 | 5306.6667 | 1326.6667
| Meter sends confirmation | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 1194000 | 1910400 | 10613.3333 | 2653.3333
| GDN enable gas supply | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 1791000 | 2865600 | 15920 | 3980
Alternative Flow:
GDNs do not receive confirmation | Failure notification | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 597000 | 955200 | 5306.6667 | 1326.6667
| Error Report | 590 | 1000 | 590000 | 944000 | 5244.4444 | 1311.1111 | 1187000 | 1899200 | 10551.1111 | 2637.7778
| Test request | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 1784000 | 2854400 | 15857.7778 | 3964.4444
| Performance report | 722 | 1000 | 722000 | 1155200 | 6417.7778 | 1604.4444 | 2506000 | 4009600 | 22275.5556 | 5568.8889
| Service restored notification | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 3103000 | 4964800 | 27582.2222 | 6895.5556
Smart Metering deems the request invalid | Failure notification | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 597000 | 955200 | 5306.6667 | 1326.6667
| Error Report | 590 | 1000 | 590000 | 944000 | 5244.4444 | 1311.1111 | 1187000 | 1899200 | 10551.1111 | 2637.7778
Use Case 04 - Display Messages from Gas Distribution Network
GDN sends notification to IHD | GDN send message to IHD | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 597000 | 955200 | 5306.6667 | 1326.6667
| meter acknowledges | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 1194000 | 1910400 | 10613.3333 | 2653.3333
Alternative Flow:
Meter fails to send confirmation message | Failure notification | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 597000 | 955200 | 5306.6667 | 1326.6667
| Error Report | 590 | 1000 | 590000 | 944000 | 5244.4444 | 1311.1111 | 1187000 | 1899200 | 10551.1111 | 2637.7778
| Test request | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 1784000 | 2854400 | 15857.7778 | 3964.4444
| Performance report | 722 | 1000 | 722000 | 1155200 | 6417.7778 | 1604.4444 | 2506000 | 4009600 | 22275.5556 | 5568.8889
| Service restored notification | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 3103000 | 4964800 | 27582.2222 | 6895.5556
Use Case 05 - Measure and Store Calorific Values at the meter
| CV value for the day | 580 | 1000 | 580000 | 928000 | 5155.5556 | 1288.8889 | 580000 | 928000 | 5155.5556 | 1288.8889
| Confirmation | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 1177000 | 1883200 | 10462.2222 | 2615.5556
(Optionally) GDN update the message | CV value for the day | 580 | 1000 | 580000 | 928000 | 5155.5556 | 1288.8889 | 580000 | 928000 | 5155.5556 | 1288.8889
| Confirmation | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 1177000 | 1883200 | 10462.2222 | 2615.5556
Alternative Flow:
1. The Smart Metering System rejects the message as invalid | Failure notification | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 597000 | 955200 | 5306.6667 | 1326.6667
| Error Report | 590 | 1000 | 590000 | 944000 | 5244.4444 | 1311.1111 | 1187000 | 1899200 | 10551.1111 | 2637.7778
| GDN resends the message | 580 | 1000 | 580000 | 928000 | 5155.5556 | 1288.8889 | 1767000 | 2827200 | 15706.6667 | 3926.6667
| Confirmation | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 2364000 | 3782400 | 21013.3333 | 5253.3333
Tampering Notification send to GDNs
| Meter sends tampering notification | 597 | 1000 | 597000 | 955200 | 5306.6667 | 1326.6667 | 597000 | 955200 | 5306.6667 | 1326.6667
TOTAL per meter - everything works well |  | 361170 |  | 361170000 | 577872000 | 3210400 | 802600 | 361170 | 577872 | 3210.4 | 802.6
TOTAL per meter - everything fails once |  | 382620 |  | 382620000 | 612192000 | 3401066.6667 | 850266.6667 | 382620 | 612192 | 3401.0667 | 850.2667